## Registers - group 1
Axon M515
Registers - group 1
Register Number
Via Unit 0 | Via Unit 1 | R/W | Data Type | Content | Bit Nr. | Category
0 | 0 | RW | Word | Analog Output Value (mV) 1.1 |  | Basic
1 | 1 | RW | Word | Analog Output Value (mV) 1.2 |  | Basic
2 | 2 | RW | Word | Analog Output Value (mV) 1.3 |  | Basic
3 | 3 | RW | Word | Analog Output Value (mV) 1.4 |  | Basic
4 - 5 | 4 - 5 | R | Word | Analog Input Value 1.1 |  | Basic
6 | 6 | RW | MixedBits | Group MasterWatchDog (MWD) Status |  | Advanced
|  |  |  | MWD Enable | 0 | Advanced
|  |  |  | MWD Reboot Detected | 1 | Advanced
7 | 7 | RW | MixedBits | User-programmable LED states | 0 | Basic
|  |  |  | User LED 1.1 | 0 | Basic
|  |  |  | User LED 1.2 | 1 | Basic
|  |  |  | User LED 1.3 | 2 | Basic
|  |  |  | User LED 1.4 | 3 | Basic
|  |  |  | User LED 1.5 | 4 | Basic
|  |  |  | User LED 1.6 | 5 | Basic
|  |  |  | User LED 1.7 | 6 | Basic
|  |  |  | User LED 1.8 | 7 | Basic
|  |  |  | User LED 1.9 | 8 | Basic
|  |  |  | User LED 1.10 | 9 | Basic
|  |  |  | User LED 1.11 | 10 | Basic
|  |  |  | User LED 1.12 | 11 | Basic
|  |  |  | User LED 1.13 | 12 | Basic
|  |  |  | User LED 1.14 | 13 | Basic
| 100 - 101 | RW | DWord | (Internal) RS485 Full Mode Configuration 1.1 |  | Obsolete
500 | 500 | W | Word | Reserved - Do Not Use |  | Reserved
501 | 501 | W | Word | Reserved - Do Not Use |  | Reserved
502 | 502 | W | Word | Reserved - Do Not Use |  | Reserved
503 | 503 | W | Word | Reserved - Do Not Use |  | Reserved
504 | 504 | W | Word | Reserved - Do Not Use |  | Reserved
505 | 505 | W | Word | Reserved - Do Not Use |  | Reserved
506 | 506 | W | Word | Reserved - Do Not Use |  | Reserved
507 | 507 | W | Word | Reserved - Do Not Use |  | Reserved
508 | 508 | W | Word | Reserved - Do Not Use |  | Reserved
509 | 509 | W | Word | Reserved - Do Not Use |  | Reserved
| 510 | RW | Word | (Internal) Stored Firmware Version |  | Expert
| 511 | RW | Word | (Internal) Stored Firmware Revision |  | Expert
| 512 | RW | Word | (Internal) Stored Base Firmware Revision |  | Expert
| 513 | RW | Word | (Internal) Stored Expanded Flash Magic Value |  | Expert
| 514 | RW | Word | (Internal) Stored PCB Revision |  | Expert
| 515 | RW | Word | (Internal) Stored PCB Serial Number |  | Expert
| 516 | RW | Word | (Internal) Stored HW Revision Number |  | Expert
1000 | 1000 | R | Word | Firmware Version |  | Expert
1001 | 1001 | R | Word | Number of I/Os |  | Advanced
|  |  |  | Number of DIs | 0 - 7 | Advanced
|  |  |  | Number of DOs | 8 - 15 | Advanced
1002 | 1002 | R | Word | Number of peripherals |  | Advanced
|  |  |  | Number of internal RS485 lines | 0 - 3 | Advanced
|  |  |  | Number of AOs | 4 - 7 | Advanced
|  |  |  | Number of AIs | 8 - 15 | Advanced
1003 | 1003 | R | Word | Firmware ID |  | Expert
1004 | 1004 | R | Word | Hardware ID |  | Expert
1005 - 1006 | 1005 - 1006 | R | DWord | PCB Serial Number |  | Expert
1007 | 1007 | RW | Word | Interrupt Mask |  | Expert
|  |  |  | RS485 RX queue not empty | 0 | Expert
|  |  |  | RS485 TX queue empty | 1 | Expert
|  |  |  | RS485 ModBus RX frame finished | 2 | Expert
|  |  |  | Digital Input changed state | 3 | Expert
1008 | 1008 | RW | Word | Group MasterWatchDog (MWD) Timeout (in 100us) |  | Advanced
1009 | 1009 | R | Word | VRef |  | Expert
1010 | 1010 | RW | Word | Analog Input Mode |  | Basic
1011 | 1011 | RW | Word | Analog Input Mode |  | Basic
1012 | 1012 | RW | Word | Analog Input Mode |  | Basic
1013 | 1013 | RW | Word | Analog Input Mode |  | Basic
| 2000 - 2219 | W | Word | Reserved - Do Not Use |  | Reserved

## Registers - group 2
Axon M515
Registers - group 2
Register Number
Via Unit 0 | Via Unit 2 | R/W | Data Type | Content | Bit Nr. | Category
100 | 0 | R | MixedBits | Digital Inputs | 0 | Basic
|  |  |  | Digital Input 2.1 | 0 | Basic
|  |  |  | Digital Input 2.2 | 1 | Basic
|  |  |  | Digital Input 2.3 | 2 | Basic
|  |  |  | Digital Input 2.4 | 3 | Basic
|  |  |  | Digital Input 2.5 | 4 | Basic
|  |  |  | Digital Input 2.6 | 5 | Basic
101 | 1 | RW | MixedBits | Digital Outputs | 0 | Basic
|  |  |  | Digital Output 2.1 | 0 | Basic
|  |  |  | Digital Output 2.2 | 1 | Basic
|  |  |  | Digital Output 2.3 | 2 | Basic
|  |  |  | Digital Output 2.4 | 3 | Basic
|  |  |  | Digital Output 2.5 | 4 | Basic
102 | 2 | RW | Word | Analog Output Value (mV) 2.1 |  | Basic
103 | 3 | RW | Word | Analog Output Value (mV) 2.2 |  | Basic
104 | 4 | RW | Word | Analog Output Value (mV) 2.3 |  | Basic
105 | 5 | RW | Word | Analog Output Value (mV) 2.4 |  | Basic
106 - 107 | 6 - 7 | R | Word | Analog Input Value 2.1 |  | Basic
108 | 8 | RW | MixedBits | Group MasterWatchDog (MWD) Status |  | Advanced
|  |  |  | MWD Enable | 0 | Advanced
|  |  |  | MWD Reboot Detected | 1 | Advanced
109 | 9 | R | Word | Length of RS485 TX Queue 2.1 |  | Obsolete
110 - 111 | 10 - 11 | RW | DWord | Counter of Digital Input 2.1 |  | Basic
112 - 113 | 12 - 13 | RW | DWord | Counter of Digital Input 2.2 |  | Basic
114 - 115 | 14 - 15 | RW | DWord | Counter of Digital Input 2.3 |  | Basic
116 - 117 | 16 - 17 | RW | DWord | Counter of Digital Input 2.4 |  | Basic
118 - 119 | 18 - 19 | RW | DWord | Counter of Digital Input 2.5 |  | Basic
120 - 121 | 20 - 21 | RW | DWord | Counter of Digital Input 2.6 |  | Basic
122 | 22 | RW | MixedBits | Synchronised Digital Output | 0 | Advanced
|  |  |  | Synchronised Digital Output 2.1 | 0 | Advanced
|  |  |  | Synchronised Digital Output 2.2 | 1 | Advanced
|  |  |  | Synchronised Digital Output 2.3 | 2 | Advanced
|  |  |  | Synchronised Digital Output 2.4 | 3 | Advanced
|  |  |  | Synchronised Digital Output 2.5 | 4 | Advanced
123 | 23 | RW | MixedBits | Synchronised Digital Output Locks | 0 | Advanced
|  |  |  | Synchronised Digital Output Lock 2.1 | 0 | Advanced
|  |  |  | Synchronised Digital Output Lock 2.2 | 1 | Advanced
|  |  |  | Synchronised Digital Output Lock 2.3 | 2 | Advanced
|  |  |  | Synchronised Digital Output Lock 2.4 | 3 | Advanced
|  |  |  | Synchronised Digital Output Lock 2.5 | 4 | Advanced
| 100 - 101 | RW | DWord | (Internal) RS485 Full Mode Configuration 2.1 |  | Obsolete
| 500 | RW | Word | RS485 TERMIOS CFlags 2.1 |  | Expert
| 501 | RW | Word | RS485 TERMIOS LFlags 2.1 |  | Expert
| 502 | RW | Word | RS485 TERMIOS IFlags 2.1 |  | Expert
| 503 | RW | Word | RS485 TERMIOS LDisc 2.1 |  | Expert
| 504 | RW | Word | RS485 ModBus Timeout 2.1 |  | Expert
605 | 505 | W | Word | Reserved - Do Not Use |  | Reserved
606 | 506 | W | Word | Reserved - Do Not Use |  | Reserved
607 | 507 | W | Word | Reserved - Do Not Use |  | Reserved
608 | 508 | W | Word | Reserved - Do Not Use |  | Reserved
609 | 509 | W | Word | Reserved - Do Not Use |  | Reserved
| 510 | RW | Word | (Internal) Stored Firmware Version |  | Expert
| 511 | RW | Word | (Internal) Stored Firmware Revision |  | Expert
| 512 | RW | Word | (Internal) Stored Base Firmware Revision |  | Expert
| 513 | RW | Word | (Internal) Stored Expanded Flash Magic Value |  | Expert
| 514 | RW | Word | (Internal) Stored PCB Revision |  | Expert
| 515 | RW | Word | (Internal) Stored PCB Serial Number |  | Expert
| 516 | RW | Word | (Internal) Stored HW Revision Number |  | Expert
1100 | 1000 | R | Word | Firmware Version |  | Expert
1101 | 1001 | R | Word | Number of I/Os |  | Advanced
|  |  |  | Number of DIs | 0 - 7 | Advanced
|  |  |  | Number of DOs | 8 - 15 | Advanced
1102 | 1002 | R | Word | Number of peripherals |  | Advanced
|  |  |  | Number of internal RS485 lines | 0 - 3 | Advanced
|  |  |  | Number of AOs | 4 - 7 | Advanced
|  |  |  | Number of AIs | 8 - 15 | Advanced
1103 | 1003 | R | Word | Firmware ID |  | Expert
1104 | 1004 | R | Word | Hardware ID |  | Expert
1105 - 1106 | 1005 - 1006 | R | DWord | PCB Serial Number |  | Expert
1107 | 1007 | RW | Word | Interrupt Mask |  | Expert
|  |  |  | RS485 RX queue not empty | 0 | Expert
|  |  |  | RS485 TX queue empty | 1 | Expert
|  |  |  | RS485 ModBus RX frame finished | 2 | Expert
|  |  |  | Digital Input changed state | 3 | Expert
1108 | 1008 | RW | Word | Group MasterWatchDog (MWD) Timeout (in 100us) |  | Advanced
1109 | 1009 | R | Word | VRef |  | Expert
1110 | 1010 | RW | Word | Debounce time (in 100us) for DI 2.1 |  | Advanced
1111 | 1011 | RW | Word | Debounce time (in 100us) for DI 2.2 |  | Advanced
1112 | 1012 | RW | Word | Debounce time (in 100us) for DI 2.3 |  | Advanced
1113 | 1013 | RW | Word | Debounce time (in 100us) for DI 2.4 |  | Advanced
1114 | 1014 | RW | Word | Debounce time (in 100us) for DI 2.5 |  | Advanced
1115 | 1015 | RW | Word | Debounce time (in 100us) for DI 2.6 |  | Advanced
1116 | 1016 | RW | MixedBits | Enable DirectSwitch functionality | 0 | Basic
|  |  |  | Enable DirectSwitch on DI 2.1 | 0 | Basic
|  |  |  | Enable DirectSwitch on DI 2.2 | 1 | Basic
|  |  |  | Enable DirectSwitch on DI 2.3 | 2 | Basic
|  |  |  | Enable DirectSwitch on DI 2.4 | 3 | Basic
|  |  |  | Enable DirectSwitch on DI 2.5 | 4 | Basic
1117 | 1017 | RW | MixedBits | Invert DirectSwitch Polarity | 0 | Basic
|  |  |  | Invert DirectSwitch polarity on DI 2.1 | 0 | Basic
|  |  |  | Invert DirectSwitch polarity on DI 2.2 | 1 | Basic
|  |  |  | Invert DirectSwitch polarity on DI 2.3 | 2 | Basic
|  |  |  | Invert DirectSwitch polarity on DI 2.4 | 3 | Basic
|  |  |  | Invert DirectSwitch polarity on DI 2.5 | 4 | Basic
1118 | 1018 | RW | MixedBits | Enabled DirectSwitch Toggle Mode | 0 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 2.1 | 0 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 2.2 | 1 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 2.3 | 2 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 2.4 | 3 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 2.5 | 4 | Basic
1119 | 1019 | RW | Word | Analog Input Mode |  | Basic
1120 | 1020 | RW | Word | Analog Input Mode |  | Basic
1121 | 1021 | RW | Word | Analog Input Mode |  | Basic
1122 | 1022 | RW | Word | Analog Input Mode |  | Basic
| 2000 - 2219 | W | Word | Reserved - Do Not Use |  | Reserved

## Coils - group 1
Axon M515
Coils - group 1
Register Number
Via Unit 0 | Via Unit 1 | R/W | Content | Category
1000 | 1000 | RW | MWD reset indication | Advanced
1002 | 1002 | R | Reset internal SoC of I/O group | Advanced
1003 | 1003 | RW | Save current configuration into flash as default | Advanced
1004 | 1004 | RW | (Internal) firmware programming toggle | Expert
1005 | 1005 | RW | (Internal) firmware reprogramming toggle | Expert
1006 | 1006 | RW | (Internal) firmware calibration programming toggle | Expert

## Coils - group 2
Axon M515
Coils - group 2
Register Number
Via Unit 0 | Via Unit 2 | R/W | Content | Category
100 | 0 | RW | Digital Output 2.1 | Basic
101 | 1 | RW | Digital Output 2.2 | Basic
102 | 2 | RW | Digital Output 2.3 | Basic
103 | 3 | RW | Digital Output 2.4 | Basic
104 | 4 | RW | Digital Output 2.5 | Basic
105 | 5 | R | Digital Input 2.1 | Basic
106 | 6 | R | Digital Input 2.2 | Basic
107 | 7 | R | Digital Input 2.3 | Basic
108 | 8 | R | Digital Input 2.4 | Basic
109 | 9 | R | Digital Input 2.5 | Basic
110 | 10 | R | Digital Input 2.6 | Basic
1100 | 1000 | RW | MWD reset indication | Advanced
1102 | 1002 | R | Reset internal SoC of I/O group | Advanced
1103 | 1003 | RW | Save current configuration into flash as default | Advanced
1104 | 1004 | RW | (Internal) firmware programming toggle | Expert
1105 | 1005 | RW | (Internal) firmware reprogramming toggle | Expert
1106 | 1006 | RW | (Internal) firmware calibration programming toggle | Expert
1107 | 1007 | RW | Enable DirectSwitch on DI 2.1 | Advanced
1108 | 1008 | RW | Enable DirectSwitch on DI 2.2 | Advanced
1109 | 1009 | RW | Enable DirectSwitch on DI 2.3 | Advanced
1110 | 1010 | RW | Enable DirectSwitch on DI 2.4 | Advanced
1111 | 1011 | RW | Enable DirectSwitch on DI 2.5 | Advanced
1112 | 1012 | RW | Invert DirectSwitch Polarity on DI 2.1 | Advanced
1113 | 1013 | RW | Invert DirectSwitch Polarity on DI 2.2 | Advanced
1114 | 1014 | RW | Invert DirectSwitch Polarity on DI 2.3 | Advanced
1115 | 1015 | RW | Invert DirectSwitch Polarity on DI 2.4 | Advanced
1116 | 1016 | RW | Invert DirectSwitch Polarity on DI 2.5 | Advanced
1117 | 1017 | RW | Enable DirectSwitch Toggle Mode on DI 2.1 | Advanced
1118 | 1018 | RW | Enable DirectSwitch Toggle Mode on DI 2.2 | Advanced
1119 | 1019 | RW | Enable DirectSwitch Toggle Mode on DI 2.3 | Advanced
1120 | 1020 | RW | Enable DirectSwitch Toggle Mode on DI 2.4 | Advanced
1121 | 1021 | RW | Enable DirectSwitch Toggle Mode on DI 2.5 | Advanced

## Description
Byte order
0-LSB, 15-MSB
AI 1 Mode Configuration
Value | Ai Mode
0 | Voltage 0 – 10V
1 | Current 0 – 20mA
AO 1 Mode Configuration
Value | Type of measurement
0 | Voltage 0 – 10V
1 | Current 0 – 20mA
3 | Resistance 0 – 2kΩ
Baud rate configuration (obsolete)
Value | Speed [bps]
11 | 2400
12 | 4800
13 | 9600
14 | 19200
15 | 38400
4097 | 57600
7098 | 115200