## Registers - section 1
Axon S205
Registers - section 1
Register Address
Via Unit 0 | Via Unit 1 | R/W | Data Type | Content | Bit Nr. | Category
0 | 0 | R | MixedBits | Digital Inputs | 0 | Basic
|  |  |  | Digital Input 1.1 | 0 | Basic
|  |  |  | Digital Input 1.2 | 1 | Basic
|  |  |  | Digital Input 1.3 | 2 | Basic
|  |  |  | Digital Input 1.4 | 3 | Basic
|  |  |  | Digital Input 1.5 | 4 | Basic
|  |  |  | Digital Input 1.6 | 5 | Basic
|  |  |  | Digital Input 1.7 | 6 | Basic
|  |  |  | Digital Input 1.8 | 7 | Basic
1 | 1 | RW | MixedBits | Relay Outputs | 0 | Basic
|  |  |  | Relay Output 1.1 | 0 | Basic
|  |  |  | Relay Output 1.2 | 1 | Basic
|  |  |  | Relay Output 1.3 | 2 | Basic
|  |  |  | Relay Output 1.4 | 3 | Basic
|  |  |  | Relay Output 1.5 | 4 | Basic
|  |  |  | Relay Output 1.6 | 5 | Basic
|  |  |  | Relay Output 1.7 | 6 | Basic
|  |  |  | Relay Output 1.8 | 7 | Basic
2 | 2 | RW | MixedBits | Section MasterWatchDog (MWD) Status |  | Advanced
|  |  |  | MWD Enable | 0 | Advanced
|  |  |  | MWD Reboot Detected | 1 | Advanced
3 - 4 | 3 - 4 | RW | DWord | Counter of Digital Input 1.1 |  | Basic
5 - 6 | 5 - 6 | RW | DWord | Counter of Digital Input 1.2 |  | Basic
7 - 8 | 7 - 8 | RW | DWord | Counter of Digital Input 1.3 |  | Basic
9 - 10 | 9 - 10 | RW | DWord | Counter of Digital Input 1.4 |  | Basic
11 - 12 | 11 - 12 | RW | DWord | Counter of Digital Input 1.5 |  | Basic
13 - 14 | 13 - 14 | RW | DWord | Counter of Digital Input 1.6 |  | Basic
15 - 16 | 15 - 16 | RW | DWord | Counter of Digital Input 1.7 |  | Basic
17 - 18 | 17 - 18 | RW | DWord | Counter of Digital Input 1.8 |  | Basic
19 | 19 | W | Word | Reserved - Do Not Use |  | Reserved
20 | 20 | W | Word | Reserved - Do Not Use |  | Reserved
21 | 21 | W | Word | Reserved - Do Not Use |  | Reserved
22 | 22 | W | Word | Reserved - Do Not Use |  | Reserved
23 | 23 | RW | MixedBits | Synchronised Digital Outputs/Relay Outputs | 0 | Advanced
|  |  |  | Synchronised DO/RO 1.1 | 0 | Advanced
|  |  |  | Synchronised DO/RO 1.2 | 1 | Advanced
|  |  |  | Synchronised DO/RO 1.3 | 2 | Advanced
|  |  |  | Synchronised DO/RO 1.4 | 3 | Advanced
|  |  |  | Synchronised DO/RO 1.5 | 4 | Advanced
|  |  |  | Synchronised DO/RO 1.6 | 5 | Advanced
|  |  |  | Synchronised DO/RO 1.7 | 6 | Advanced
|  |  |  | Synchronised DO/RO 1.8 | 7 | Advanced
24 | 24 | RW | MixedBits | Synchronised Digital Output/Relay Output Locks | 0 | Advanced
|  |  |  | Synchronised DO/RO Lock 1.1 | 0 | Advanced
|  |  |  | Synchronised DO/RO Lock 1.2 | 1 | Advanced
|  |  |  | Synchronised DO/RO Lock 1.3 | 2 | Advanced
|  |  |  | Synchronised DO/RO Lock 1.4 | 3 | Advanced
|  |  |  | Synchronised DO/RO Lock 1.5 | 4 | Advanced
|  |  |  | Synchronised DO/RO Lock 1.6 | 5 | Advanced
|  |  |  | Synchronised DO/RO Lock 1.7 | 6 | Advanced
|  |  |  | Synchronised DO/RO Lock 1.8 | 7 | Advanced
| 100 - 101 | RW | DWord | (Internal) RS485 Full Mode Configuration 1.1 |  | Obsolete
500 | 500 | W | Word | Reserved - Do Not Use |  | Reserved
501 | 501 | W | Word | Reserved - Do Not Use |  | Reserved
502 | 502 | W | Word | Reserved - Do Not Use |  | Reserved
503 | 503 | W | Word | Reserved - Do Not Use |  | Reserved
504 | 504 | W | Word | Reserved - Do Not Use |  | Reserved
505 | 505 | W | Word | Reserved - Do Not Use |  | Reserved
506 | 506 | W | Word | Reserved - Do Not Use |  | Reserved
507 | 507 | W | Word | Reserved - Do Not Use |  | Reserved
508 | 508 | W | Word | Reserved - Do Not Use |  | Reserved
509 | 509 | W | Word | Reserved - Do Not Use |  | Reserved
| 510 | RW | Word | (Internal) Stored Firmware Version |  | Expert
| 511 | RW | Word | (Internal) Stored Firmware Revision |  | Expert
| 512 | RW | Word | (Internal) Stored Base Firmware Revision |  | Expert
| 513 | RW | Word | (Internal) Stored Expanded Flash Magic Value |  | Expert
| 514 | RW | Word | (Internal) Stored PCB Revision |  | Expert
| 515 | RW | Word | (Internal) Stored PCB Serial Number |  | Expert
| 516 | RW | Word | (Internal) Stored HW Revision Number |  | Expert
1000 | 1000 | R | Word | Firmware Version |  | Expert
1001 | 1001 | R | Word | Number of I/Os |  | Advanced
|  |  |  | Number of DIs | 0 - 7 | Advanced
|  |  |  | Number of DOs | 8 - 15 | Advanced
1002 | 1002 | R | Word | Number of peripherals |  | Advanced
|  |  |  | Number of internal RS485 lines | 0 - 3 | Advanced
|  |  |  | Number of AOs | 4 - 7 | Advanced
|  |  |  | Number of AIs | 8 - 15 | Advanced
1003 | 1003 | R | Word | Firmware ID |  | Expert
1004 | 1004 | R | Word | Hardware ID |  | Expert
1005 - 1006 | 1005 - 1006 | R | DWord | PCB Serial Number |  | Expert
1007 | 1007 | RW | Word | Interrupt Mask |  | Expert
|  |  |  | RS485 RX queue not empty | 0 | Expert
|  |  |  | RS485 TX queue empty | 1 | Expert
|  |  |  | RS485 ModBus RX frame finished | 2 | Expert
|  |  |  | Digital Input changed state | 3 | Expert
1008 | 1008 | RW | Word | Section MasterWatchDog (MWD) Timeout (in 1ms) |  | Advanced
1009 | 1009 | R | Word | VRef of MCU |  | Expert
1010 | 1010 | RW | Word | Debounce time (in 100us) for DI 1.1 |  | Advanced
1011 | 1011 | RW | Word | Debounce time (in 100us) for DI 1.2 |  | Advanced
1012 | 1012 | RW | Word | Debounce time (in 100us) for DI 1.3 |  | Advanced
1013 | 1013 | RW | Word | Debounce time (in 100us) for DI 1.4 |  | Advanced
1014 | 1014 | RW | Word | Debounce time (in 100us) for DI 1.5 |  | Advanced
1015 | 1015 | RW | Word | Debounce time (in 100us) for DI 1.6 |  | Advanced
1016 | 1016 | RW | Word | Debounce time (in 100us) for DI 1.7 |  | Advanced
1017 | 1017 | RW | Word | Debounce time (in 100us) for DI 1.8 |  | Advanced
1018 | 1018 | RW | MixedBits | Enable DirectSwitch functionality | 0 | Basic
|  |  |  | Enable DirectSwitch on DI 1.1 | 0 | Basic
|  |  |  | Enable DirectSwitch on DI 1.2 | 1 | Basic
|  |  |  | Enable DirectSwitch on DI 1.3 | 2 | Basic
|  |  |  | Enable DirectSwitch on DI 1.4 | 3 | Basic
|  |  |  | Enable DirectSwitch on DI 1.5 | 4 | Basic
|  |  |  | Enable DirectSwitch on DI 1.6 | 5 | Basic
|  |  |  | Enable DirectSwitch on DI 1.7 | 6 | Basic
|  |  |  | Enable DirectSwitch on DI 1.8 | 7 | Basic
1019 | 1019 | RW | MixedBits | Invert DirectSwitch Polarity | 0 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 1.1 | 0 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 1.2 | 1 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 1.3 | 2 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 1.4 | 3 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 1.5 | 4 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 1.6 | 5 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 1.7 | 6 | Basic
|  |  |  | Invert DirectSwitch Polarity on DI 1.8 | 7 | Basic
1020 | 1020 | RW | MixedBits | Enabled DirectSwitch Toggle | 0 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 1.1 | 0 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 1.2 | 1 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 1.3 | 2 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 1.4 | 3 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 1.5 | 4 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 1.6 | 5 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 1.7 | 6 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 1.8 | 7 | Basic
1021 | 1021 | W | Word | Reserved - Do Not Use |  | Reserved
1022 | 1022 | W | Word | Reserved - Do Not Use |  | Reserved
| 2000 - 2219 | W | Word | Reserved - Do Not Use |  | Reserved
4000 | 4000 | R | Word | Storage - Erase cycles used [%] |  | Basic
4001 | 4001 | R | Word | Storage - Good blocks [%] |  | Basic

## Coils - section 1
Axon S205
Coils - section 1
Register Address
Via Unit 0 | Via Unit 1 | R/W | Content | Category
0 | 0 | RW | Relay Output 1.1 | Basic
1 | 1 | RW | Relay Output 1.2 | Basic
2 | 2 | RW | Relay Output 1.3 | Basic
3 | 3 | RW | Relay Output 1.4 | Basic
4 | 4 | RW | Relay Output 1.5 | Basic
5 | 5 | RW | Relay Output 1.6 | Basic
6 | 6 | RW | Relay Output 1.7 | Basic
7 | 7 | RW | Relay Output 1.8 | Basic
8 | 8 | R | Digital Input 1.1 | Basic
9 | 9 | R | Digital Input 1.2 | Basic
10 | 10 | R | Digital Input 1.3 | Basic
11 | 11 | R | Digital Input 1.4 | Basic
12 | 12 | R | Digital Input 1.5 | Basic
13 | 13 | R | Digital Input 1.6 | Basic
14 | 14 | R | Digital Input 1.7 | Basic
15 | 15 | R | Digital Input 1.8 | Basic
1000 | 1000 | RW | MWD reset indication | Advanced
1001 | 1001 | RW | Enable/Disable 1Wire Bus | Advanced
1002 | 1002 | RW | Reset section MCU | Advanced
1003 | 1003 | RW | Save current configuration and use on startup | Advanced
1004 | 1004 | RW | (Internal) Firmware programming toggle | Expert
1005 | 1005 | RW | (Internal) Firmware reprogramming toggle | Expert
1006 | 1006 | RW | (Internal) Firmware calibration programming toggle | Expert
1007 | 1007 | RW | Enable DirectSwitch on DI 1.1 | Advanced
1008 | 1008 | RW | Enable DirectSwitch on DI 1.2 | Advanced
1009 | 1009 | RW | Enable DirectSwitch on DI 1.3 | Advanced
1010 | 1010 | RW | Enable DirectSwitch on DI 1.4 | Advanced
1011 | 1011 | RW | Enable DirectSwitch on DI 1.5 | Advanced
1012 | 1012 | RW | Enable DirectSwitch on DI 1.6 | Advanced
1013 | 1013 | RW | Enable DirectSwitch on DI 1.7 | Advanced
1014 | 1014 | RW | Enable DirectSwitch on DI 1.8 | Advanced
1015 | 1015 | RW | Invert DirectSwitch Polarity on DI 1.1 | Advanced
1016 | 1016 | RW | Invert DirectSwitch Polarity on DI 1.2 | Advanced
1017 | 1017 | RW | Invert DirectSwitch Polarity on DI 1.3 | Advanced
1018 | 1018 | RW | Invert DirectSwitch Polarity on DI 1.4 | Advanced
1019 | 1019 | RW | Invert DirectSwitch Polarity on DI 1.5 | Advanced
1020 | 1020 | RW | Invert DirectSwitch Polarity on DI 1.6 | Advanced
1021 | 1021 | RW | Invert DirectSwitch Polarity on DI 1.7 | Advanced
1022 | 1022 | RW | Invert DirectSwitch Polarity on DI 1.8 | Advanced
1023 | 1023 | RW | Enable DirectSwitch Toggle Mode on DI 1.1 | Advanced
1024 | 1024 | RW | Enable DirectSwitch Toggle Mode on DI 1.2 | Advanced
1025 | 1025 | RW | Enable DirectSwitch Toggle Mode on DI 1.3 | Advanced
1026 | 1026 | RW | Enable DirectSwitch Toggle Mode on DI 1.4 | Advanced
1027 | 1027 | RW | Enable DirectSwitch Toggle Mode on DI 1.5 | Advanced
1028 | 1028 | RW | Enable DirectSwitch Toggle Mode on DI 1.6 | Advanced
1029 | 1029 | RW | Enable DirectSwitch Toggle Mode on DI 1.7 | Advanced
1030 | 1030 | RW | Enable DirectSwitch Toggle Mode on DI 1.8 | Advanced

## Description
Visit Unipi Knowledge base for more information
| Byte order |  | Brief protocol description: | • Unipi PLCs (Neuron,Axon,Patron) uses the ModBus TCP protocol to provide access to I/Os
| 0-LSB, 15-MSB |  |  | • ModbusTCP provides access to all I/Os except 1Wire and RS485/RS232 and other buses and serial lines
• By default the server listens only on local loopback, if needed it is possible to let it listen on all interfaces by changing its systemd script
• ModBus word size is 16 bits
• ModBus uses big endian byte encoding
Analog Input Configuration(U/I) |  |  |  | • Integer variables of type Word and DWord are always unsigned, type Int is signed and corresponds to a single word
Value | Ai Mode |  |  | • Multiple-word values are encoded as big endian memory as well - from a little-endian perspective a 64bit byte parsing order is 78563412
0 | Voltage 0 – 10V |  |  | • Floating point values are encoded in the IEEE 754 half-precision format, with big-endian byte order
1 | Current 0 – 20mA |  |  | • Double-precision floating point values are encoded in the IEEE 754 single-precision format, with the same byte order as multi-word integers
• QModMaster is a useful tool for exploring ModBus encoding and communication
• For more information about ModBus see: http://www.simplymodbus.ca/
Analog Input Configuration(U/I/R)
Value | Ai Mode
0 | Off
1 | Voltage 0 – 10 V
2 | Voltage 0 – 2.5 V
3 | Current 0 – 20 mA
4 | Resistance (three conductors) 0 – 1 960 Ω
5 | Resistance (two conductors) 0 – 100 kΩ
Analog Output Configuration(U/I/R-measure)
Value | Type of measurement
0 | Voltage 0 – 10V
1 | Current 0 – 20mA
3 | Resistance 0 – 2kΩ
Baud rate configuration (obsolete)
Value | Speed [bps]
11 | 2400
12 | 4800
13 | 9600
14 | 19200
15 | 38400
4097 | 57600
4098 | 115200
Storage
Content | Description
Storage Life - Erase cycles used [%]
Storage Life - Good blocks [%]
Storage - Power cycles | Unipi Neuron only - depends on the model of microSD card
Storage - Vendor specific 1-3 | Unipi Neuron only - depends on the model of microSD card
microSD card vendor/model | Storage - Vendor specific 1 | Storage - Vendor specific 2 | Storage - Vendor specific 3
Swissbit pSLC | card series (0 = S-2x, 1 = S-4x) | Number of unrecoverable CRC errors | Wear level threshold %
Connection status (LTE)
Content | Description
Connection - Mode | 0 = WAN_STATE_INIT 1 = WAN_STATE_LTE_ON 2 = WAN_STATE_LTE_OFF 3 = WAN_STATE_ETH_ON 4 = WAN_STATE_LTE_ON_ETH_OFF 5 = WAN_STATE_LTE_OFF_ETH_ON 6 = WAN_STATE_LTE_ON_ETH_ON 7 = WAN_STATE_LTE_OFF_ETH_OFF 8 = WAN_STATE_ETH_OFF
Connection - Network type | 0 = GSM 1 = GSM COMPACT 2 = UTRAN 3 = GSM/GPRS with EDGE availability 4 = UTRAN with HSDPA availability 5 = UTRAN with HSUPA availability 6 = UTRAN with HSDPA and HSUPA availability 7 = LTE
Connection - RSSI [dBm] | -48 dBm .. -99 dBm
Connection - Signal quality | 0 (good) - 7 (bad) 99 (unknown)