## Registers - group 1
Neuron xS30
Registers - group 1
Register Number
Via Unit 0 | Via Unit 1 | R/W | Data Type | Content | Bit Nr. | Category
0 | 0 | R | MixedBits | Digital Inputs | 0 | Basic
|  |  |  | Digital Input 1.1 | 0 | Basic
|  |  |  | Digital Input 1.2 | 1 | Basic
|  |  |  | Digital Input 1.3 | 2 | Basic
|  |  |  | Digital Input 1.4 | 3 | Basic
|  |  |  | Digital Input 1.5 | 4 | Basic
|  |  |  | Digital Input 1.6 | 5 | Basic
|  |  |  | Digital Input 1.7 | 6 | Basic
|  |  |  | Digital Input 1.8 | 7 | Basic
|  |  |  | Digital Input 1.9 | 8 | Basic
|  |  |  | Digital Input 1.10 | 9 | Basic
|  |  |  | Digital Input 1.11 | 10 | Basic
|  |  |  | Digital Input 1.12 | 11 | Basic
|  |  |  | Digital Input 1.13 | 12 | Basic
|  |  |  | Digital Input 1.14 | 13 | Basic
|  |  |  | Digital Input 1.15 | 14 | Basic
|  |  |  | Digital Input 1.16 | 15 | Basic
1 | 1 | R | MixedBits | Digital Input 1.17 | 0 | Basic
|  |  |  | Digital Input 1.18 | 1 | Basic
|  |  |  | Digital Input 1.19 | 2 | Basic
|  |  |  | Digital Input 1.20 | 3 | Basic
|  |  |  | Digital Input 1.21 | 4 | Basic
|  |  |  | Digital Input 1.22 | 5 | Basic
|  |  |  | Digital Input 1.23 | 6 | Basic
|  |  |  | Digital Input 1.24 | 7 | Basic
2 | 2 | RW | MixedBits | Group MasterWatchDog (MWD) Status |  | Advanced
|  |  |  | MWD Enable | 0 | Advanced
|  |  |  | MWD Reboot Detected | 1 | Advanced
3 - 4 | 3 - 4 | RW | DWord | Counter of Digital Input 1.1 |  | Basic
5 - 6 | 5 - 6 | RW | DWord | Counter of Digital Input 1.2 |  | Basic
7 - 8 | 7 - 8 | RW | DWord | Counter of Digital Input 1.3 |  | Basic
9 - 10 | 9 - 10 | RW | DWord | Counter of Digital Input 1.4 |  | Basic
11 - 12 | 11 - 12 | RW | DWord | Counter of Digital Input 1.5 |  | Basic
13 - 14 | 13 - 14 | RW | DWord | Counter of Digital Input 1.6 |  | Basic
15 - 16 | 15 - 16 | RW | DWord | Counter of Digital Input 1.7 |  | Basic
17 - 18 | 17 - 18 | RW | DWord | Counter of Digital Input 1.8 |  | Basic
19 - 20 | 19 - 20 | RW | DWord | Counter of Digital Input 1.9 |  | Basic
21 - 22 | 21 - 22 | RW | DWord | Counter of Digital Input 1.10 |  | Basic
23 - 24 | 23 - 24 | RW | DWord | Counter of Digital Input 1.11 |  | Basic
25 - 26 | 25 - 26 | RW | DWord | Counter of Digital Input 1.12 |  | Basic
27 - 28 | 27 - 28 | RW | DWord | Counter of Digital Input 1.13 |  | Basic
29 - 30 | 29 - 30 | RW | DWord | Counter of Digital Input 1.14 |  | Basic
31 - 32 | 31 - 32 | RW | DWord | Counter of Digital Input 1.15 |  | Basic
33 - 34 | 33 - 34 | RW | DWord | Counter of Digital Input 1.16 |  | Basic
35 - 36 | 35 - 36 | RW | DWord | Counter of Digital Input 1.17 |  | Basic
37 - 38 | 37 - 38 | RW | DWord | Counter of Digital Input 1.18 |  | Basic
39 - 40 | 39 - 40 | RW | DWord | Counter of Digital Input 1.19 |  | Basic
41 - 42 | 41 - 42 | RW | DWord | Counter of Digital Input 1.20 |  | Basic
43 - 44 | 43 - 44 | RW | DWord | Counter of Digital Input 1.21 |  | Basic
45 - 46 | 45 - 46 | RW | DWord | Counter of Digital Input 1.22 |  | Basic
47 - 48 | 47 - 48 | RW | DWord | Counter of Digital Input 1.23 |  | Basic
49 - 50 | 49 - 50 | RW | DWord | Counter of Digital Input 1.24 |  | Basic
51 | 51 | RW | MixedBits | User-programmable LED states | 0 | Basic
|  |  |  | User LED 1.1 | 0 | Basic
|  |  |  | User LED 1.2 | 1 | Basic
|  |  |  | User LED 1.3 | 2 | Basic
|  |  |  | User LED 1.4 | 3 | Basic
| 100 - 101 | RW | DWord | (Internal) RS485 Full Mode Configuration 1.1 |  | Obsolete
| 500 | RW | Word | RS485 TERMIOS CFlags 1.1 |  | Expert
| 501 | RW | Word | RS485 TERMIOS LFlags 1.1 |  | Expert
| 502 | RW | Word | RS485 TERMIOS IFlags 1.1 |  | Expert
| 503 | RW | Word | RS485 TERMIOS LDisc 1.1 |  | Expert
| 504 | RW | Word | RS485 ModBus Timeout 1.1 |  | Expert
505 | 505 | W | Word | Reserved - Do Not Use |  | Reserved
506 | 506 | W | Word | Reserved - Do Not Use |  | Reserved
507 | 507 | W | Word | Reserved - Do Not Use |  | Reserved
508 | 508 | W | Word | Reserved - Do Not Use |  | Reserved
509 | 509 | W | Word | Reserved - Do Not Use |  | Reserved
| 510 | RW | Word | (Internal) Stored Firmware Version |  | Expert
| 511 | RW | Word | (Internal) Stored Firmware Revision |  | Expert
| 512 | RW | Word | (Internal) Stored Base Firmware Revision |  | Expert
| 513 | RW | Word | (Internal) Stored Expanded Flash Magic Value |  | Expert
| 514 | RW | Word | (Internal) Stored PCB Revision |  | Expert
| 515 | RW | Word | (Internal) Stored PCB Serial Number |  | Expert
| 516 | RW | Word | (Internal) Stored HW Revision Number |  | Expert
1000 | 1000 | R | Word | Firmware Version |  | Expert
1001 | 1001 | R | Word | Number of I/Os |  | Advanced
|  |  |  | Number of DIs | 0 - 7 | Advanced
|  |  |  | Number of DOs | 8 - 15 | Advanced
1002 | 1002 | R | Word | Number of peripherals |  | Advanced
|  |  |  | Number of internal RS485 lines | 0 - 3 | Advanced
|  |  |  | Number of AOs | 4 - 7 | Advanced
|  |  |  | Number of AIs | 8 - 15 | Advanced
1003 | 1003 | R | Word | Firmware ID |  | Expert
1004 | 1004 | R | Word | Hardware ID |  | Expert
1005 - 1006 | 1005 - 1006 | R | DWord | PCB Serial Number |  | Expert
1007 | 1007 | RW | Word | Interrupt Mask |  | Expert
|  |  |  | RS485 RX queue not empty | 0 | Expert
|  |  |  | RS485 TX queue empty | 1 | Expert
|  |  |  | RS485 ModBus RX frame finished | 2 | Expert
|  |  |  | Digital Input changed state | 3 | Expert
1008 | 1008 | RW | Word | Group MasterWatchDog (MWD) Timeout (in 100us) |  | Advanced
1009 | 1009 | R | Word | VRef |  | Expert
1010 | 1010 | RW | Word | Debounce time (in 100us) for DI 1.1 |  | Advanced
1011 | 1011 | RW | Word | Debounce time (in 100us) for DI 1.2 |  | Advanced
1012 | 1012 | RW | Word | Debounce time (in 100us) for DI 1.3 |  | Advanced
1013 | 1013 | RW | Word | Debounce time (in 100us) for DI 1.4 |  | Advanced
1014 | 1014 | RW | Word | Debounce time (in 100us) for DI 1.5 |  | Advanced
1015 | 1015 | RW | Word | Debounce time (in 100us) for DI 1.6 |  | Advanced
1016 | 1016 | RW | Word | Debounce time (in 100us) for DI 1.7 |  | Advanced
1017 | 1017 | RW | Word | Debounce time (in 100us) for DI 1.8 |  | Advanced
1018 | 1018 | RW | Word | Debounce time (in 100us) for DI 1.9 |  | Advanced
1019 | 1019 | RW | Word | Debounce time (in 100us) for DI 1.10 |  | Advanced
1020 | 1020 | RW | Word | Debounce time (in 100us) for DI 1.11 |  | Advanced
1021 | 1021 | RW | Word | Debounce time (in 100us) for DI 1.12 |  | Advanced
1022 | 1022 | RW | Word | Debounce time (in 100us) for DI 1.13 |  | Advanced
1023 | 1023 | RW | Word | Debounce time (in 100us) for DI 1.14 |  | Advanced
1024 | 1024 | RW | Word | Debounce time (in 100us) for DI 1.15 |  | Advanced
1025 | 1025 | RW | Word | Debounce time (in 100us) for DI 1.16 |  | Advanced
1026 | 1026 | RW | Word | Debounce time (in 100us) for DI 1.17 |  | Advanced
1027 | 1027 | RW | Word | Debounce time (in 100us) for DI 1.18 |  | Advanced
1028 | 1028 | RW | Word | Debounce time (in 100us) for DI 1.19 |  | Advanced
1029 | 1029 | RW | Word | Debounce time (in 100us) for DI 1.20 |  | Advanced
1030 | 1030 | RW | Word | Debounce time (in 100us) for DI 1.21 |  | Advanced
1031 | 1031 | RW | Word | Debounce time (in 100us) for DI 1.22 |  | Advanced
1032 | 1032 | RW | Word | Debounce time (in 100us) for DI 1.23 |  | Advanced
1033 | 1033 | RW | Word | Debounce time (in 100us) for DI 1.24 |  | Advanced
1034 | 1034 | RW | MixedBits | RS485 Mode Configuration |  | Advanced
|  |  |  | Baud rate | 0 - 12 | Advanced
|  |  |  | Parity enable | 13 | Advanced
|  |  |  | Parity-0=Even, 1=Odd | 14 | Advanced
|  |  |  | Modbus RTU support enabled (interrupt) | 15 | Advanced
1035 | 1035 | RW | MixedBits | RS485 Address Configuration |  | Advanced
| 2000 - 2219 | W | Word | Reserved - Do Not Use |  | Reserved

## Coils - group 1
Neuron xS30
Coils - group 1
Register Number
Via Unit 0 | Via Unit 1 | R/W | Content | Category
0 | 0 | R | Digital Input 1.1 | Basic
1 | 1 | R | Digital Input 1.2 | Basic
2 | 2 | R | Digital Input 1.3 | Basic
3 | 3 | R | Digital Input 1.4 | Basic
4 | 4 | R | Digital Input 1.5 | Basic
5 | 5 | R | Digital Input 1.6 | Basic
6 | 6 | R | Digital Input 1.7 | Basic
7 | 7 | R | Digital Input 1.8 | Basic
8 | 8 | R | Digital Input 1.9 | Basic
9 | 9 | R | Digital Input 1.10 | Basic
10 | 10 | R | Digital Input 1.11 | Basic
11 | 11 | R | Digital Input 1.12 | Basic
12 | 12 | R | Digital Input 1.13 | Basic
13 | 13 | R | Digital Input 1.14 | Basic
14 | 14 | R | Digital Input 1.15 | Basic
15 | 15 | R | Digital Input 1.16 | Basic
16 | 16 | R | Digital Input 1.17 | Basic
17 | 17 | R | Digital Input 1.18 | Basic
18 | 18 | R | Digital Input 1.19 | Basic
19 | 19 | R | Digital Input 1.20 | Basic
20 | 20 | R | Digital Input 1.21 | Basic
21 | 21 | R | Digital Input 1.22 | Basic
22 | 22 | R | Digital Input 1.23 | Basic
23 | 23 | R | Digital Input 1.24 | Basic
24 | 24 | RW | User Programmable LED 1.1 | Basic
25 | 25 | RW | User Programmable LED 1.2 | Basic
26 | 26 | RW | User Programmable LED 1.3 | Basic
27 | 27 | RW | User Programmable LED 1.4 | Basic
1000 | 1000 | RW | MWD reset indication | Advanced
1002 | 1002 | R | Reset internal SoC of I/O group | Advanced
1003 | 1003 | RW | Save current configuration into flash as default | Advanced
1004 | 1004 | RW | (Internal) firmware programming toggle | Expert
1005 | 1005 | RW | (Internal) firmware reprogramming toggle | Expert
1006 | 1006 | RW | (Internal) firmware calibration programming toggle | Expert

## Description
Byte order
0-LSB, 15-MSB
AI 1 Mode Configuration
Value | Ai Mode
0 | Voltage 0 – 10V
1 | Current 0 – 20mA
AO 1 Mode Configuration
Value | Type of measurement
0 | Voltage 0 – 10V
1 | Current 0 – 20mA
3 | Resistance 0 – 2kΩ
Baud rate configuration (obsolete)
Value | Speed [bps]
11 | 2400
12 | 4800
13 | 9600
14 | 19200
15 | 38400
4097 | 57600
7098 | 115200