## Registers - group 1
Neuron xS50
Registers - group 1
Register Number
Via Unit 0 | Via Unit 1 | R/W | Data Type | Content | Bit Nr. | Category
0 | 0 | R | MixedBits | Digital Inputs | 0 | Basic
|  |  |  | Digital Input 1.1 | 0 | Basic
|  |  |  | Digital Input 1.2 | 1 | Basic
|  |  |  | Digital Input 1.3 | 2 | Basic
|  |  |  | Digital Input 1.4 | 3 | Basic
|  |  |  | Digital Input 1.5 | 4 | Basic
|  |  |  | Digital Input 1.6 | 5 | Basic
1 | 1 | RW | MixedBits | Digital Outputs | 0 | Basic
|  |  |  | Digital Output 1.1 | 0 | Basic
|  |  |  | Digital Output 1.2 | 1 | Basic
|  |  |  | Digital Output 1.3 | 2 | Basic
|  |  |  | Digital Output 1.4 | 3 | Basic
|  |  |  | Digital Output 1.5 | 4 | Basic
2 | 2 | RW | Word | Analog Output Value (mV) 1.1 |  | Basic
3 | 3 | RW | Word | Analog Output Value (mV) 1.2 |  | Basic
4 | 4 | RW | Word | Analog Output Value (mV) 1.3 |  | Basic
5 | 5 | RW | Word | Analog Output Value (mV) 1.4 |  | Basic
6 - 7 | 6 - 7 | R | Word | Analog Input Value 1.1 |  | Basic
8 | 8 | RW | MixedBits | Group MasterWatchDog (MWD) Status |  | Advanced
|  |  |  | MWD Enable | 0 | Advanced
|  |  |  | MWD Reboot Detected | 1 | Advanced
9 - 10 | 9 - 10 | RW | DWord | Counter of Digital Input 1.1 |  | Basic
11 - 12 | 11 - 12 | RW | DWord | Counter of Digital Input 1.2 |  | Basic
13 - 14 | 13 - 14 | RW | DWord | Counter of Digital Input 1.3 |  | Basic
15 - 16 | 15 - 16 | RW | DWord | Counter of Digital Input 1.4 |  | Basic
17 - 18 | 17 - 18 | RW | DWord | Counter of Digital Input 1.5 |  | Basic
19 - 20 | 19 - 20 | RW | DWord | Counter of Digital Input 1.6 |  | Basic
21 | 21 | RW | MixedBits | Synchronised Digital Output | 0 | Advanced
|  |  |  | Synchronised Digital Output 1.1 | 0 | Advanced
|  |  |  | Synchronised Digital Output 1.2 | 1 | Advanced
|  |  |  | Synchronised Digital Output 1.3 | 2 | Advanced
|  |  |  | Synchronised Digital Output 1.4 | 3 | Advanced
|  |  |  | Synchronised Digital Output 1.5 | 4 | Advanced
22 | 22 | RW | MixedBits | Synchronised Digital Output Locks | 0 | Advanced
|  |  |  | Synchronised Digital Output Lock 1.1 | 0 | Advanced
|  |  |  | Synchronised Digital Output Lock 1.2 | 1 | Advanced
|  |  |  | Synchronised Digital Output Lock 1.3 | 2 | Advanced
|  |  |  | Synchronised Digital Output Lock 1.4 | 3 | Advanced
|  |  |  | Synchronised Digital Output Lock 1.5 | 4 | Advanced
| 100 - 101 | RW | DWord | (Internal) RS485 Full Mode Configuration 1.1 |  | Obsolete
| 500 | RW | Word | RS485 TERMIOS CFlags 1.1 |  | Expert
| 501 | RW | Word | RS485 TERMIOS LFlags 1.1 |  | Expert
| 502 | RW | Word | RS485 TERMIOS IFlags 1.1 |  | Expert
| 503 | RW | Word | RS485 TERMIOS LDisc 1.1 |  | Expert
| 504 | RW | Word | RS485 ModBus Timeout 1.1 |  | Expert
505 | 505 | W | Word | Reserved - Do Not Use |  | Reserved
506 | 506 | W | Word | Reserved - Do Not Use |  | Reserved
507 | 507 | W | Word | Reserved - Do Not Use |  | Reserved
508 | 508 | W | Word | Reserved - Do Not Use |  | Reserved
509 | 509 | W | Word | Reserved - Do Not Use |  | Reserved
| 510 | RW | Word | (Internal) Stored Firmware Version |  | Expert
| 511 | RW | Word | (Internal) Stored Firmware Revision |  | Expert
| 512 | RW | Word | (Internal) Stored Base Firmware Revision |  | Expert
| 513 | RW | Word | (Internal) Stored Expanded Flash Magic Value |  | Expert
| 514 | RW | Word | (Internal) Stored PCB Revision |  | Expert
| 515 | RW | Word | (Internal) Stored PCB Serial Number |  | Expert
| 516 | RW | Word | (Internal) Stored HW Revision Number |  | Expert
1000 | 1000 | R | Word | Firmware Version |  | Expert
1001 | 1001 | R | Word | Number of I/Os |  | Advanced
|  |  |  | Number of DIs | 0 - 7 | Advanced
|  |  |  | Number of DOs | 8 - 15 | Advanced
1002 | 1002 | R | Word | Number of peripherals |  | Advanced
|  |  |  | Number of internal RS485 lines | 0 - 3 | Advanced
|  |  |  | Number of AOs | 4 - 7 | Advanced
|  |  |  | Number of AIs | 8 - 15 | Advanced
1003 | 1003 | R | Word | Firmware ID |  | Expert
1004 | 1004 | R | Word | Hardware ID |  | Expert
1005 - 1006 | 1005 - 1006 | R | DWord | PCB Serial Number |  | Expert
1007 | 1007 | RW | Word | Interrupt Mask |  | Expert
|  |  |  | RS485 RX queue not empty | 0 | Expert
|  |  |  | RS485 TX queue empty | 1 | Expert
|  |  |  | RS485 ModBus RX frame finished | 2 | Expert
|  |  |  | Digital Input changed state | 3 | Expert
1008 | 1008 | RW | Word | Group MasterWatchDog (MWD) Timeout (in 100us) |  | Advanced
1009 | 1009 | R | Word | VRef |  | Expert
1010 | 1010 | RW | Word | Debounce time (in 100us) for DI 1.1 |  | Advanced
1011 | 1011 | RW | Word | Debounce time (in 100us) for DI 1.2 |  | Advanced
1012 | 1012 | RW | Word | Debounce time (in 100us) for DI 1.3 |  | Advanced
1013 | 1013 | RW | Word | Debounce time (in 100us) for DI 1.4 |  | Advanced
1014 | 1014 | RW | Word | Debounce time (in 100us) for DI 1.5 |  | Advanced
1015 | 1015 | RW | Word | Debounce time (in 100us) for DI 1.6 |  | Advanced
1016 | 1016 | RW | MixedBits | Enable DirectSwitch functionality | 0 | Basic
|  |  |  | Enable DirectSwitch on DI 1.1 | 0 | Basic
|  |  |  | Enable DirectSwitch on DI 1.2 | 1 | Basic
|  |  |  | Enable DirectSwitch on DI 1.3 | 2 | Basic
|  |  |  | Enable DirectSwitch on DI 1.4 | 3 | Basic
|  |  |  | Enable DirectSwitch on DI 1.5 | 4 | Basic
1017 | 1017 | RW | MixedBits | Invert DirectSwitch Polarity | 0 | Basic
|  |  |  | Invert DirectSwitch polarity on DI 1.1 | 0 | Basic
|  |  |  | Invert DirectSwitch polarity on DI 1.2 | 1 | Basic
|  |  |  | Invert DirectSwitch polarity on DI 1.3 | 2 | Basic
|  |  |  | Invert DirectSwitch polarity on DI 1.4 | 3 | Basic
|  |  |  | Invert DirectSwitch polarity on DI 1.5 | 4 | Basic
1018 | 1018 | RW | MixedBits | Enabled DirectSwitch Toggle Mode | 0 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 1.1 | 0 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 1.2 | 1 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 1.3 | 2 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 1.4 | 3 | Basic
|  |  |  | Enable DirectSwitch Toggle on DI 1.5 | 4 | Basic
1019 | 1019 | RW | Word | Analog Input Mode |  | Basic
1020 | 1020 | RW | Word | Analog Input Mode |  | Basic
1021 | 1021 | RW | Word | Analog Input Mode |  | Basic
1022 | 1022 | RW | Word | Analog Input Mode |  | Basic
1023 | 1023 | RW | MixedBits | RS485 Mode Configuration |  | Advanced
|  |  |  | Baud rate | 0 - 12 | Advanced
|  |  |  | Parity enable | 13 | Advanced
|  |  |  | Parity-0=Even, 1=Odd | 14 | Advanced
|  |  |  | Modbus RTU support enabled (interrupt) | 15 | Advanced
1024 | 1024 | RW | MixedBits | RS485 Address Configuration |  | Advanced
| 2000 - 2219 | W | Word | Reserved - Do Not Use |  | Reserved

## Coils - group 1
Neuron xS50
Coils - group 1
Register Number
Via Unit 0 | Via Unit 1 | R/W | Content | Category
0 | 0 | RW | Digital Output 1.1 | Basic
1 | 1 | RW | Digital Output 1.2 | Basic
2 | 2 | RW | Digital Output 1.3 | Basic
3 | 3 | RW | Digital Output 1.4 | Basic
4 | 4 | RW | Digital Output 1.5 | Basic
5 | 5 | R | Digital Input 1.1 | Basic
6 | 6 | R | Digital Input 1.2 | Basic
7 | 7 | R | Digital Input 1.3 | Basic
8 | 8 | R | Digital Input 1.4 | Basic
9 | 9 | R | Digital Input 1.5 | Basic
10 | 10 | R | Digital Input 1.6 | Basic
1000 | 1000 | RW | MWD reset indication | Advanced
1002 | 1002 | R | Reset internal SoC of I/O group | Advanced
1003 | 1003 | RW | Save current configuration into flash as default | Advanced
1004 | 1004 | RW | (Internal) firmware programming toggle | Expert
1005 | 1005 | RW | (Internal) firmware reprogramming toggle | Expert
1006 | 1006 | RW | (Internal) firmware calibration programming toggle | Expert
1007 | 1007 | RW | Enable DirectSwitch on DI 1.1 | Advanced
1008 | 1008 | RW | Enable DirectSwitch on DI 1.2 | Advanced
1009 | 1009 | RW | Enable DirectSwitch on DI 1.3 | Advanced
1010 | 1010 | RW | Enable DirectSwitch on DI 1.4 | Advanced
1011 | 1011 | RW | Enable DirectSwitch on DI 1.5 | Advanced
1012 | 1012 | RW | Invert DirectSwitch Polarity on DI 1.1 | Advanced
1013 | 1013 | RW | Invert DirectSwitch Polarity on DI 1.2 | Advanced
1014 | 1014 | RW | Invert DirectSwitch Polarity on DI 1.3 | Advanced
1015 | 1015 | RW | Invert DirectSwitch Polarity on DI 1.4 | Advanced
1016 | 1016 | RW | Invert DirectSwitch Polarity on DI 1.5 | Advanced
1017 | 1017 | RW | Enable DirectSwitch Toggle Mode on DI 1.1 | Advanced
1018 | 1018 | RW | Enable DirectSwitch Toggle Mode on DI 1.2 | Advanced
1019 | 1019 | RW | Enable DirectSwitch Toggle Mode on DI 1.3 | Advanced
1020 | 1020 | RW | Enable DirectSwitch Toggle Mode on DI 1.4 | Advanced
1021 | 1021 | RW | Enable DirectSwitch Toggle Mode on DI 1.5 | Advanced

## Description
Byte order
0-LSB, 15-MSB
AI 1 Mode Configuration
Value | Ai Mode
0 | Voltage 0 – 10V
1 | Current 0 – 20mA
AO 1 Mode Configuration
Value | Type of measurement
0 | Voltage 0 – 10V
1 | Current 0 – 20mA
3 | Resistance 0 – 2kΩ
Baud rate configuration (obsolete)
Value | Speed [bps]
11 | 2400
12 | 4800
13 | 9600
14 | 19200
15 | 38400
4097 | 57600
7098 | 115200